## Data Sheet
Electric Heater Data Sheet
1 | CUSTOMER |  |  |  |  | JOB/REFERENCE NUMBER
2 | END USER |  |  |  |  | PROPOSAL NUMBER
3 | PLANT LOCATION |  |  |  |  | ITEM NUMBER
4 | SERVICE OF UNIT |  |  |  |  | DATE | [6 empty] | REV
5 | SIZE |  | TYPE | [5 empty] | CONNECTED IN |  |  |  | SER | PAR
6 | SQ. FT. SURFACE/UNIT |  |  |  | SHELLS/UNIT |  |  |  |  | SQ. FT. SURFACE/SHELL
7 | PERFORMANCE OF ONE UNIT
8 | FLUID NAME
9 | FLUID QUANTITY
10 | VAPOR (IN/OUT)
11 | LIQUID (IN/OUT)
12 | TEMPERATURE (IN/OUT)
13 | DENSITY
14 | VISCOSITY
15 | SPECIFIC HEAT
16 | THERMAL CONDUCTIVITY
17 | LATENT HEAT
18 | INLET PRESSURE
19 | VELOCITY
20 | PRESSURE DROP (ALLOW/CALC)
21 | SHEATH TEMPERATURE
22 | HEAT EXCHANGED
23 | WATT DENSITY
24 | CONSTRUCTION OF ONE SHELL
25 | DESIGN/TEST PRESSURE
26 | DESIGN TEMPERATURE
27 | NUMBER PASSES PER SHELL
28 | SHELL CORROSION ALLOWANCE
29 | INLET CONNECTION SIZE/RATING
30 | OUTLET CONNECTION SIZE/RATING
31 | INTERMEDIATE CONN. SIZE/RATING
32 | NUMBER ELEMENTS |  |  | OD |  |  | HOT LENGTH | [5 empty] | COLD LENGTH
33 | ELEMENT TYPE | Tubular - Bare | [5 empty] | SHEATH MATERIAL
34 | SHELL MATERIAL |  |  |  | NOM | [5 empty] | ID
35 | HEATER FLANGE MATERIAL | [6 empty] | STANDOFF
36 | BAFFLES - CROSS | [6 empty] | SPACING
37 | BAFFLES - LONG | [6 empty] | SHELL GASKET
38 | CODE REQUIREMENTS
39 | ELECTRICAL / CONTROLS
40 | HEATER VOLTAGE |  |  |  | PHASE | [5 empty] | FREQUENCY
41 | CONTROLS VOLTAGE |  |  |  | PHASE | [5 empty] | FREQUENCY
42 | HEATER AREA CLASS. |  |  | GRP |  | ENCLOSURE
43 | CONTROLS AREA CLASS. |  |  | GRP |  | ENCLOSURE | [6 empty] | PURGE
44 | CONTROL TYPE |  |  |  |  | SUPPLIED BY
45 | NUMBER CIRCUITS |  |  | SHEATH THERMOCOUPLE | [7 empty] | QTY. REQ.
46 | REMARKS
47
48
49
50

## Area Classification
Classes
The class defines the general nature of hazardous material in the surrounding atmosphere.
Class | Hazardous Material in Surrounding Atmosphere
I | Hazardous because flammable gases or vapors are present in the air in quantities sufficient to produce explosive or ignitable mixtures.
II | Hazardous because combustible or conductive dusts are present.
III | Hazardous because ignitable fibers or flying's are present, but not likely to be in suspension in sufficient quantities to produce ignitable mixtures. Typical wood chips, cotton, flax and nylon. Group classifications are not applied to this class.
Divisions
The division defines the probability of hazardous material being present in an ignitable concentration in the surrounding atmosphere.
Division | Presence of Hazardous Material
1 | The substance referred to by class is present during normal conditions.
2 | The substance referred to by class is present only in abnormal conditions, such as a container failure or system breakdown.
Groups
The group defines the hazardous material in the surrounding atmosphere.
Group | Hazardous Material in Surrounding Atmosphere
A | Acetylene
B | Hydrogen, fuel and combustible process gases containing more than 30% hydrogen by volume or gases of equivalent hazard such as butadiene, ethylene, oxide, propylene oxide and acrolein.
C | Carbon monoxide, ether, hydrogen sulfide, morphline, cyclopropane, ethyl and ethylene or gases of equivalent hazard.
D | Gasoline, acetone, ammonia, benzene, butane, cyclopropane, ethanol, hexane, methanol, methane, vinyl chloride, natural gas, naphtha, propane or gases of equivalent hazard.
E | Combustible metal dusts, including aluminum, magnesium and their commercial alloys or other combustible dusts whose particle size, abrasiveness and conductivity present similar hazards in connection with electrical equipment.
F | Carbonaceous dusts, carbon black, coal black, charcoal, coal or coke dusts that have more than 8% total entrapped volatiles or dusts that have been sesitized by other material so they present an explosion hazard.
G | Flour dust, grain dust, flour, starch, sugar, wood, plastic and chemicals.
Temperature Code
A mixture of hazardous gases and air may ignite in contact with a hot surface. The condition for ignition depends on several factors as surface area, temperature and concentration of gas.
Equipment approved receives a temperature code indicating the maximum surface temperature of the equipment.
Temperature Code | Maximum Surface Temperature |  | Equipment that does not exceed a maximum surface temperature of 212 °F (104 °F ambient temperature) is not required to be marked with a temperature code (NEC).
- | °F | °C
T1 | 842 | 450
T2 | 572 | 300
T2A | 536 | 280
T2B | 500 | 260
T2C | 446 | 230
T2D | 419 | 215
T3 | 392 | 200
T3A | 356 | 180
T3B | 329 | 165
T3C | 320 | 160
T4 | 275 | 135
T4A | 248 | 120
T5 | 212 | 100
T6 | 185 | 85
Recommended Reading Material
• National Electrical Code, NFPA 70, Chapter 5, Article 500
• 29 CFR 1910 Subpart S, Electrical 1910.307
• NFPA 497, "Classification of Gases, Vapors, and Dusts for Electrical Equipment in Hazardous Classified Locations"
• NFPA Handbook, "Electrical Installations in Hazardous Locations, " by P. J. Schram and M. W. Earley
• NFPA 70E, Chapter 5, "Hazardous (Classified) Locations"
• NFPA 325, "Fire Hazard Properties of Flammable Liquids, Gases, and Volatile Solids"
• ANSI/UL 913, "Intrinsically Safe Apparatus"
• NFPA 496, "Purged and Pressurized Enclosure for Electrical Equipment in Hazardous Locations."

## NEMA
NEMA Non-Hazardous Locations
Type | Description
1 | Intended for use primarily to provide a degree of protection against limited amounts of falling dirt.
3 | Intended for outdoor use primarily to provide a degree of protection against rain, sleet, windblown dust, and damage from external ice formation.
3R | Intended for outdoor use primarily to provide a degree of protection against rain, sleet, and damage from external ice formation.
3S | Intended for outdoor use primarily to provide a degree of protection against rain, sleet, windblown dust, and to provide for operation of external mechanisms when ice laden.
4 | Intended for indoor or outdoor use primarily to provide a degree of protection against windblown dust and rain, splashing water, hose-directed water, and damage from external ice formation.
4X | Intended for indoor or outdoor use primarily to provide a degree of protection against corrosion, windblown dust and rain, splashing water, hose-directed water, and damage from ice formation.
6 | Intended for indoor or outdoor use primarily to provide a degree of protection against hose directed water, the entry of water during occasional temporary submersion at a limited depth, and damage from external ice formation.
6P | Intended for indoor or outdoor use primarily to provide a degree of protection against hose directed water, the entry of water during prolonged submersion at a limited depth, and damage from external ice formation.
12 | Intended for indoor use primarily to provide a degree of protection against circulating dust, falling dirt, and dripping non-corrosive liquids.
12K | Type 12 with knockouts.
NEMA Hazardous Locations
Type | Description
7 | Intended for indoor use in locations classified as Class I, Groups A, B, C, or D, as defined in the National Electrical Code.
8 | Intended for indoor or outdoor use in locations classified as Class I, Groups A, B, C, or D, as defined in the National Electrical Code.
9 | Intended for indoor use in locations classified as Class II, Groups E, F, or G, as defined in the National Electrical Code.
10 | Constructed to meet the applicable requirements of the Mine Safety and Health Administration.
Reference: www.nema.org, NEMA Standards Publication No. 250